## Cover
CST Value Proposition Study
Simple 3 Cost Factor CST Cost Model
|  |  | Project Number: | FIS0000048
Index
1 | Read Me
2 | Calculation
3 | Regional Cost Factors
4 | Annual Cost Reduction
Revision Table
Project: | FIS0000048 |  | Name | Date
Datum: | 2022-02-16 | Prepared | Kretschmann, Johannes | 2023-02-16
Rev.: | 2 | Checked | Dr. Lovegrove Keith | 2023-02-16
Description |  | Revision | Date | Prepared | Checked
Draft (no cost adder) |  | 0 | 2023-02-13 | MPU | KRT
Final Draft |  | 1 | 2023-02-15 | KRT | LOV
Final |  | 2 | 2023-03-10 | KRT | LOV
Contact
Johannes Kretschmann
Projects Director, Head of CSP
Johannes.Kretschmann@fichtner.de

## Read Me
Introduction:
This cost calculation tool has been prepared in order to allow for a simple cost determination of a CST plant in Australia. Besides the region within Australia and the year of the contract award, only the three main determining plant parameters are required as input:
- Solar field thermal capacity in MWt;
- Thermal energy storage (TES) capacity in MWh; and
- Power Block capacity in MWe.
Specific cost figures have been determined for a solar tower reference plant, based in NSW (medium regional cost adder - NSW medium), using a more complex cost model. Using this cost model, the total overnight cost are calculated and broken down into the three cost portions solar field, thermal energy storage and power block. I.e. the derived specific cost figures for the reference plant include both direct and indirect cost.
Further, scaling exponents are provided for each of the three cost portions. Providing the new plant configuration, i.e. capacities for each portion, the new cost figures are calculated, applying the scaling exponents on the specific cost figures of the reference plant.
Basis of Estimate:
The underlying cost data, cost adders and scaling exponents are based on a number of international CST projects, budget quotes and recent stakeholder engagement, incl. Vast Solar, Cosin, BSE, Sener, JC, NREL, IRENA. The reference cost data has been normalized and international cost data transferred, applying exchange and country factors (Compass International).
Based on the assumption of an EPC procurement, a total of 20% of indirect cost are considered for the EPC cost. On top of the EPC a total of 5% of owner’s cost are added, incl. land cost, development cost, utility connections and additional owner’s cost during construction and commissioning.
Given the global supply chain issue and related cost escalations, also reflected in the Draft 2023 Inputs, Assumptions and Scenarios Report, to be used in AEMO’s 2023/2024 Forecasting and Planning publications for the NEM, an additional escalation factor of 13% is considered. Given there is little recent CST cost data available, a similar cost escalation as for a CCGT plant has been considered.
Regional Factors:
Regional factors have been derived from AEMO’s Draft 2023 Inputs, Assumptions and Scenarios Report. For WA and NT (not included in theAEMO’s Draft 2023 Inputs, Assumptions and Scenarios Report), the source referenced behind the data is used.
As Australian reference location, in order to convert international cost data to Australia, a remote location in NSW is considered. I.e. the “NSW medium” region is the reference region and all other regions are scaled accordingly. This is important to note, as the reference region used in the Draft 2023 Inputs, Assumptions and Scenarios Report is VIC low. I.e. when determining the reference cost data equivalent to the Draft 2023 Inputs, Assumptions and Scenarios Report VIC low must be selected.
Future Cost Reduction:
The provided cost reduction curve is based on the latest IEA World Energy Outlook and the provided CST deployment projection as part of the Announced Pledges Scenario (APS) Scenario. For the learning rate 15% is considered until 2035 and thereafter 10%.

## Calculation
New Plant Configuration
Item | Unit | Value [Unit] | Specific Cost [A$/UNIT] | Total Cost [mA$] | Factor
Financial Year FID | - | 2023 |  |  | 100%
Region | - | NSW medium |  |  | 100% | Item | Value | 1 | 2 | 3 | 4
Power block | MWe | 140 | 2028795.1393 | 284031319.5 |  | For Solar Multiple | 1 | 0.8 | 12 | 1.6 | 2
Thermal energy Storage | MWh | 5000 | 35510.7381 | 177553690.3139 |  | For Storage hours | 15 | 8 | 12 | 16 | 20
Solar Field | MWt | 900 | 627208.5918 | 564487732.5759 |  | Choose TES Capacity [MWh] | 5000
Total Plant | MWe | 140 | 7329091.0171 | 1026072742.3898 |  | Choose Solar Field Capacity [MW] | 333.3333
Turbine efficiency net | - | 0.42
Storage hours | h | 15
Solar multiple | - | 2.7
Reference Plant
Item | Unit | Reference Value [Unit] | Specific Cost [A$/Unit] | Total Cost [A$] | Scaling Exponent [-]
Financial Year FID | - | 2023
Region | - | NSW Med
Power block | MWe | 140 | 2028795.1393 | 284031319.5 | 0.7
Thermal energy Storage | MWh | 4667 | 35879.76 | 167450839.92 | 0.85
Solar Field | MWt | 720 | 644230.3791 | 463845872.9646 | 0.88
Total Plant | MWe | 140 | 6538057.3742 | 915328032.3846
Turbine efficiency net | - | 0.42
Storage hours | h | 14.001
Solar multiple | - | 2.16
Note to user; primary inputs are light blue cells only, Year, region Power Block net capacity, TES capacity and Solar Field capacity in cells C3 - C7 . To achieve specific solar multiple or storage hours for the selected power block capacity use values suggested in J7 and J8. Please note that a solar field capacity of 900 MWt is regarded as current limit for a single tower arrangement.

## Aurecon
DNI | 2500 | 2200 | 2800
SF Area (m²/Mwe) | 11000 | 12000 | 10000
Specific plant cost $/m2 | 600
Specific plant cost $/Kwe | 6600 | 7200 | 6000
Reference Project
Capacity net Mwe | 180
Capacity gross Mwe | 200
Field size | 2200000
Total EPC | 1320000000

## Regional Cost Factors
Weighted Regional cost factors (as per AEMO ISP Assumptions, referenced to NSW medium)
Region | Regional Factor | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs | O&M costs | Comment / Source
Vic low | 94.12% | 95.24% | 93.16% | 100% | 90.77% | 92.62% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Vic medium | 96.94% | 98.1% | 95.96% | 100% | 93.49% | 95.4% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Vic high | 98.83% | 100% | 97.82% | 100% | 95.31% | 97.25% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Qld low | 94.12% | 95.24% | 93.16% | 100% | 90.77% | 92.62% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Qld medium | 101.2% | 100% | 102.9% | 100% | 104.8% | 103.9% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Qld high | 108.3% | 104.8% | 112.7% | 100% | 118.8% | 116% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
NSW low | 94.12% | 95.24% | 93.16% | 100% | 90.77% | 92.62% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
NSW medium | 100% | 100% | 100% | 100% | 100% | 100% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
NSW high | 105.9% | 104.8% | 107.7% | 100% | 109.2% | 108.2% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
SA Low | 94.12% | 95.24% | 93.16% | 100% | 90.77% | 92.62% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
SA medium | 101% | 100% | 102.4% | 100% | 104.1% | 103.6% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
SA high | 107.9% | 104.8% | 111.6% | 100% | 117.5% | 114.6% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
WA low | 92.77% | 95.24% | 90.6% | 100% | 85.38% | 88.52% | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fwww.aemo.com.au%2F-%2Fmedia%2FFiles%2FElectricity%2FNEM%2FPlanning_and_Forecasting%2FInputs-Assumptions-Methodologies%2F2019%2FGHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb&wdOrigin=BROWSELINK
WA medium | 101.7% | 100% | 104.3% | 100% | 106.9% | 105.7% | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fwww.aemo.com.au%2F-%2Fmedia%2FFiles%2FElectricity%2FNEM%2FPlanning_and_Forecasting%2FInputs-Assumptions-Methodologies%2F2019%2FGHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb&wdOrigin=BROWSELINK
WA high | 110.7% | 104.8% | 117.9% | 100% | 128.5% | 123% | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fwww.aemo.com.au%2F-%2Fmedia%2FFiles%2FElectricity%2FNEM%2FPlanning_and_Forecasting%2FInputs-Assumptions-Methodologies%2F2019%2FGHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb&wdOrigin=BROWSELINK
NT low | 95.85% | 95.24% | 96.58% | 100% | 97.69% | 97.54% | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fwww.aemo.com.au%2F-%2Fmedia%2FFiles%2FElectricity%2FNEM%2FPlanning_and_Forecasting%2FInputs-Assumptions-Methodologies%2F2019%2FGHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb&wdOrigin=BROWSELINK
NT medium | 105.6% | 100% | 112.8% | 100% | 122.3% | 116.4% | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fwww.aemo.com.au%2F-%2Fmedia%2FFiles%2FElectricity%2FNEM%2FPlanning_and_Forecasting%2FInputs-Assumptions-Methodologies%2F2019%2FGHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb&wdOrigin=BROWSELINK
NT high | 115.1% | 104.8% | 128.2% | 100% | 146.2% | 136.1% | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fwww.aemo.com.au%2F-%2Fmedia%2FFiles%2FElectricity%2FNEM%2FPlanning_and_Forecasting%2FInputs-Assumptions-Methodologies%2F2019%2FGHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb&wdOrigin=BROWSELINK
Tas low | 94.12% | 95.24% | 93.16% | 100% | 90.77% | 92.62% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Tas medium | 100% | 100% | 99.43% | 100% | 100.1% | 100.6% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Tas high | 105.9% | 104.8% | 106.6% | 100% | 109.4% | 108.5% | AEMO Draft 2023 Inputs, Assumptions and Scenarios Report
Technology Cost breakdown ratios
Technology | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs
Solar Thermal (15hrs Storage) | 75% | 0% | 0% | 25%

## Annual Cost Reduction
Year | Cost Reduction
2023 | 100%
2024 | 96.23%
2025 | 92.46%
2026 | 88.68%
2027 | 84.91%
2028 | 81.14%
2029 | 77.37%
2030 | 73.6%
2031 | 71.05%
2032 | 68.5%
2033 | 65.95%
2034 | 63.41%
2035 | 60.86%
2036 | 59.45%
2037 | 58.04%
2038 | 56.63%
2039 | 55.21%
2040 | 53.8%
2041 | 53.34%
2042 | 52.87%
2043 | 52.4%
2044 | 51.94%
2045 | 51.47%
2046 | 51.03%
2047 | 50.58%
2048 | 50.13%
2049 | 49.69%
2050 | 49.24%